## med air sizing
Estimated Medical Air Peak Flow Requirements - stated in SCFM
Simultaneous
Quantity | Location of Air Outlet | Per Room | Per Bed | Per Outlet | Per Unit | Use Factor | SCFM
Anesthetizing:
special procedure (transplant, cardiovascular, orthopedics, etc
0 |  | 0.5 |  |  |  | 100% | 0
0 | major surgery | 0.5 |  |  |  | 100% | 0
0 | delivery / C section | 0.5 |  |  |  | 100% | 0
0 | minor surgery | 0.5 |  |  |  | 75% | 0
0 | emergency surgery | 0.5 |  |  |  | 50% | 0
0 | cardiac catheterization | 0.5 |  |  |  | 50% | 0
0 | endoscopy | 0.5 |  |  |  | 10% | 0
0 | radiology | 0.5 |  |  |  | 10% | 0
Acute Care:
0 | neonatal ICU |  | 1.5 |  |  | 75% | 0
0 | ICU/CCU/PICU |  | 2 |  |  | 50% | 0
0 | recovery room (PACU, OB) |  | 2 |  |  | 25% | 0
0 | emergency room |  | 2 |  |  | 10% | 0
Subacute Care:
0 | respiratory therapy | 1 |  |  |  | 50% | 0
0 | patient room | 0.5 |  |  |  | 10% | 0
0 | pre-op holding |  |  | 1.5 |  | 10% | 0
0 | exam, treatment, donor room | 1 |  |  |  | 10% | 0
0 | dialysis, radiology |  |  | 0.5 |  | 10% | 0
0 | well baby nursery | 0.5 |  |  |  | 25% | 0
0 | birthing / LDRP | 1 |  |  |  | 50% | 0
0 | stress test (EEG & EKG) |  |  | 1 |  | 50% | 0
0 | pulmonary function lab |  |  | 1 |  | 50% | 0
0 | patient isolation |  | 0.5 |  |  | 25% | 0
Other Care Areas:
0 | anesthesia work room | 1.5 |  |  |  | 10% | 0
0 | nursery work room | 1.5 |  |  |  | 10% | 0
0 | respiratory work room | 1.5 |  |  |  | 10% | 0
0 | cast room | 0.5 |  |  |  | 10% | 0
0 | autopsy | 1 |  |  |  | 10% | 0
0 | equipment repair | 1.5 |  |  |  | 10% | 0
Medical Equipment:
0 | ventilators ** |  |  |  | 3.5 | 100% | 0
0 | pediatric croup tents |  |  |  | 2 | 50% | 0
[6 empty] | Sub Total: | 0
|  |  |  | Desiccant dryer purge % |  | 15% | 0
|  |  |  | Future expansion? insert % (##) |  | 0% | 0
|  |  |  | High altitude multiplier? insert % (##) |  | 0% | 0
(see separate sheet for high altitude adjusments)
[6 empty] | Grand Total Required SCFM | 0
** check with ventilator manufacturer for specific flow requirements
(##) does not include added capacity for dryer purge