## vacuum sizing
Estimated Medical Vacuum Peak Flow Requirements - stated in SCFM
Simultaneous
Quantity | Location of Vacuum Inlet | Per Room | Per Bed | Per Inlet | Use Factor | SCFM
Anesthetizing:
special procedure (transplant, cardiovascular, orthopedics, etc
0 |  | 4 |  |  | 100% | 0
0 | major surgery | 3.5 |  |  | 100% | 0
0 | delivery / C section | 1 |  |  | 100% | 0
0 | waste anesthetic gas disposal | 1 |  |  | 100% | 0
0 | emergency surgery | 3 |  |  | 100% | 0
0 | endoscopy | 2 |  |  | 100% | 0
0 | minor surgery | 1 |  |  | 50% | 0
0 | cardiac catheterization | 1 |  |  | 10% | 0
Acute Care:
0 | emergency room |  | 1 |  | 100% | 0
0 | ICU/CCU/PICU |  | 2 |  | 75% | 0
0 | neonatal ICU |  | 1 |  | 50% | 0
0 | OB recovery room |  | 2 |  | 50% | 0
0 | recovery room (PACU) |  | 3 |  | 50% | 0
Subacute Care:
0 | ER cast room |  | 1 |  | 50% | 0
0 | patient room - surgical |  | 1.5 |  | 50% | 0
0 | dialysis, radiology |  | 1.5 |  | 25% | 0
0 | pre-op holding |  | 1 |  | 10% | 0
0 | patient room - medical |  | 1 |  | 10% | 0
0 | birthing / LDRP |  | 1 |  | 10% | 0
0 | stress test (EEG & EKG) |  | 1 |  | 10% | 0
0 | nursery (premature) |  |  | 1 | 25% | 0
0 | respiratory therapy |  |  | 1.5 | 10% | 0
0 | exam, treatment, donor room |  |  | 1 | 10% | 0
0 | well baby nursery |  |  | 1 | 10% | 0
Other Care Areas:
0 | autopsy / morgue |  |  | 2 | 20% | 0
0 | sterile / centrile supply |  |  | 1.5 | 10% | 0
0 | anesthesia work room |  |  | 1.5 | 10% | 0
0 | medical lab / pharmacy |  |  | 1 | 10% | 0
0 | equipment repair |  |  | 1.5 | 10% | 0
[5 empty] | Sub Total: | 0
|  |  |  | Future expansion? insert % | 0% | 0
|  |  |  | High altitude multiplier? insert % | 0% | 0
(see separate sheet for high altitude adjusments)
[5 empty] | Grand Total Required SCFM | 0

## altitude compensation
Altitude Compensation Chart for Medical Vacuum
| Altitude (feet) | Atmosheric Pressure (gauge) | Additional % added
| sea level | 29.92" Hg | 0
| 500 | 29.39" Hg | 2%
| 1000 | 28.86" Hg | 4%
| 1500 | 28.33" Hg | 6%
| 2000 | 27.82" Hg | 8%
| 2500 | 27.32" Hg | 10%
| 3000 | 26.82" Hg | 12%
| 3500 | 26.33" Hg | 14%
| 4000 | 25.84" Hg | 16%
| 5000 | 24.90" Hg | 20%
| 6000 | 23.98" Hg | 25%
| 7000 | 23.09" Hg | 30%
| 8000 | 22.23" Hg | 35%
| 9000 | 21.39" Hg | 40%
| 10000 | 20.58" Hg | 45%